NASH HEALTHCARE CONSULTING AMBULATORY & OUTPATIENT EDITION

Most Frequently Cited Joint Commission Ambulatory Standards

Outpatient readers, this one is for you. Ambulatory clinics are held to the same standards as the hospital down the street, but with a fraction of the staff and rarely anyone whose entire job is compliance. That is exactly why it pays to know where surveyors are landing right now.

This analysis evaluates the Joint Commission Requirement for Improvement from five recent unannounced full ambulatory surveys, totaling 26 findings, including the SAFER® matrix.

THE HEADLINE The physical environment and life safety findings included utilities, fire systems, hazardous materials, and egress. Not one of the 26 findings reached the High-likelihood tier, but due to multiple findings in one organization, escalated to a Leadership standard.

About This Analysis

Five organizations were surveyed under the Ambulatory program, with the Primary Care Medical Home option selected. All five received Requirements for Improvement.

Surveys of this kind are small samples, not national data sets. Read where the surveyor's attention is concentrating in outpatient settings, and as a prompt to go look at your survey preparation process.

The Numbers at a Glance

- 26 total findings across five surveys

- 61.5 percent of all findings fell in the Environment of Care chapter. Add Life Safety, and the physical environment accounts for 69 percent of everything cited.

- EC.02.05.01, EP 9. The most frequently cited single item, appearing in three of the five organizations, breakers labeled SPARE were found in the ON position.

- Zero High-risk placements. No finding was placed in the High-likelihood row of the SAFER® matrix. Eleven findings landed in the Moderate row, where Leadership Involvement and Preventive Analysis enter the ESC, and where surveyors may revisit the issue in later surveys.

- Primary Care Medical Home (PCMH) exposure was concentrated. Only one organization drew findings under the PCMH-option Elements of Performance, but it drew three at once: health literacy, work history, and self-management goals.

Where the Findings Landed

| Standard Chapter | Findings | Share | Notes |
| --- | --- | --- | --- |
| Environment of Care (EC) | 16 | 61.5% | Utilities, fire protection systems, hazardous materials, ventilation |
| Life Safety (LS) | 2 | 7.7% | Egress locking and hazardous area protection |
| Record of Care (RC) | 2 | 7.7% | Both PCMH-option record content EPs |
| Medication Management (MM) | 2 | 7.7% | High-alert labeling; antimicrobial stewardship data |
| Rights and Responsibilities (RI) | 1 | 3.8% | Informed consent, laterality documentation |
| Human Resources (HR) | 1 | 3.8% | Safety orientation before care delivery |
| Leadership (LD) | 1 | 3.8% | Oversight of policy implementation |
| Provision of Care (PC) | 1 | 3.8% | PCMH-option health literacy assessment |
| Total | 26 | 100% | Across five unannounced ambulatory surveys |

Every Finding, by Standard and Element of Performance

Ordered within each chapter by SAFER® risk, highest first.

| Standard | EP | What the EP addresses | What surveyors documented | SAFER® Placement | Sites |
| --- | --- | --- | --- | --- | --- |
| Environment of Care (EC) — 16 findings |  |  |  |  |  |
| EC.02.02.01 | 5 | Risks in selecting, handling, storing, and disposing of hazardous chemicals | Eyewash station lacked the pressure to lift its dust covers; the same defect had been recorded in weekly checks for roughly six months with no corrective action. None of the three stations examined had temperature monitoring or a mixing valve. | Moderate / Widespread | 1 |
| EC.02.03.05 | 3 | Annual testing of duct, heat, and smoke detectors and manual pull stations | The device inventory did not reconcile with the number of devices actually installed so it could not be determined which devices had been tested and passed. | Moderate / Widespread | 1 |
| EC.02.03.05 | 5 | Annual testing of equipment that notifies off-site fire responders | No documentation that off-site responder notification equipment had been tested in the prior 12 months. | Moderate / Widespread | 1 |
| EC.02.05.07 | 1 | Monthly 30-second functional test of emergency lighting and exit signs | Monthly test records showed a list of failed egress lights including ten failures in a single month, with no documented action taken on any of them. | Moderate / Widespread | 1 |
| EC.02.05.01 | 7 | Pressure relationships, air exchanges, filtration, humidity, and temperature in contaminant-control areas | Airflow from the sub-sterile area was positive to the operating room, reversing the required relationship. | Moderate / Limited | 1 |
| EC.02.05.07 | 6 | Generator load requirements and the annual supplemental load test | The annual load bank test fell outside the required 12-month plus-or-minus-30-day window; the make-up test was still pending at the time of survey. | Moderate / Limited | 1 |
| EC.02.02.01 | 11 | Permits, licenses, manifests, and safety data sheets for hazardous materials and waste | The staff member who signed biohazardous waste manifests on three separate occasions had no evidence of the required EPA training. | Low / Widespread | 1 |
| EC.02.05.05 | 3 | Inspection, testing, and maintenance of utility systems, with documented dates and results | Generator fuel analyses in two buildings returned sulfur and conductivity values outside the normal range across multiple years, and no evidence showed the results were identified, evaluated, or acted upon. An entire year of results was missing. | Low / Widespread | 1 |
| EC.02.03.05 | 4 | Annual testing of visual and audible fire alarm devices, with documented results | At one site a device was listed as untested with the notation that it could not be accessed. At another, the contractor certified that all horns and strobes passed but supplied no device inventory to support the count. | Low / Widespread Low / Limited | 2 |
| EC.02.02.01 | 7 | Risks associated with selection and use of hazardous energy sources | Lead aprons were not uniquely numbered as organizational policy required; one year of inspection records was unavailable, and a memo referencing failed shielding did not identify which or how many aprons failed. | Low / Pattern | 1 |
| EC.02.03.01 | 1 | Minimizing potential harm from fire, smoke, and products of combustion | Five escutcheon rings were misaligned, leaving gaps between the sprinkler heads and the ceiling; a sprinkler head in the immunization clinic was dusty. | Low / Limited | 1 |
| EC.02.03.05 | 28 | Required documentation elements for fire alarm and fire protection maintenance, testing, and inspection | The quarterly tamper and waterflow switch inspection report omitted the referenced NFPA standard, one of the seven required documentation elements. | Low / Limited | 1 |
| EC.02.05.01 | 9 | Labeling of utility system controls to support partial or complete emergency shutdown | The single most repeated citation in this sample. At three separate organizations, breakers labeled SPARE were found energized in the ON position, three in an office clinic, several in two panels at another site, and seven in one of six panels at a third, where the panel legend was also inaccurate. | Low / Limited | 3 |
| Life Safety (LS) — 2 findings |  |  |  |  |  |
| LS.03.01.20 | 1 | Egress doors free of locks or latches requiring a tool, key, or special knowledge | A door marked as an exit, with an illuminated exit sign above it and directional signage routing occupants toward it, required an access control card to exit. Interim life safety measures were put in place. | Moderate / Limited | 1 |
| LS.03.01.30 | 3 | Hazardous area enclosure and self-closing or automatic-closing doors | A patient room converted to a storeroom had no self-closer on the door. Interim life safety measures were put in place. | Low / Limited | 1 |
| Clinical, Leadership, and Record Standards — 8 findings |  |  |  |  |  |
| RI.01.03.01 | 1 | Following a written informed consent policy | In four of eight records reviewed, the consent document did not state whether the procedure was left, right, or bilateral. Laterality applied in each case. | Moderate / Pattern | 1 |
| HR.01.04.01 | 1 | Orientation to key safety content before staff provide care | Five of eleven competency files contained no documentation that the staff member had been oriented to key safety content before delivering care. | Moderate / Pattern | 1 |
| LD.04.01.07 | 1 | Leaders review, approve, and manage implementation of policies and procedures | The governing body and leadership were cited for failing to effectively manage implementation of environment of care policies, with the volume of EC findings elsewhere in the report serving as the evidence. | Moderate / Pattern | 1 |
| MM.09.01.03 | 5 | Collecting, analyzing, and reporting antimicrobial stewardship goal data to leaders and prescribers | No antimicrobial stewardship goal was set for one calendar year, and none was developed until late in the following year. A single month of data collection and reporting existed. | Moderate / Pattern | 1 |
| PC.02.03.01 | 30 | PCMH: interdisciplinary team identifies the patient’s health literacy needs | Four of five closed records contained no documentation of health literacy needs. | Low / Widespread | 1 |
| RC.02.01.01 | 25 | PCMH: clinical record contains gender, family history, and work history including occupational exposures | Three of five closed records had no documentation of work history or occupational risk factors and exposures. | Low / Widespread | 1 |
| RC.02.01.01 | 26 | PCMH: clinical record includes self-management goals and progress toward them | None of four closed records for patients with chronic disease contained self-management goals. | Low / Widespread | 1 |
| MM.01.01.03 | 2 | Process for managing high-alert and hazardous medications | Local anesthetics containing epinephrine on the organization’s own high-alert list were stored in the dental clinic without the required high-alert labeling. Labeling was corrected before the surveyors exited. | Low / Limited | 1 |

SAFER® Matrix Distribution

All 26 findings plotted by likelihood of harm and scope. The bottom-left corner is the low-consequence corner; risk rises as findings move up and to the right.

| Likelihood to Harm | Limited | Pattern | Widespread |
| --- | --- | --- | --- |
| High | 0 | 0 | 0 |
| Moderate | 3 | 4 | 4 |
| Low | 8 | 1 | 6 |

Most findings scored in Low/Limited, isolated, low-consequence observations. The second-largest cluster is Low / Widespread, indicating the same low-risk problem was recurring across the organization as a system issue; eleven findings reached the Moderate row, each of which requires Leadership involvement in the Evidence of Standards Compliance and is reviewed at future surveys.

Five Takeaways for Outpatient Clinics

1. The electrical panel.

Three of five organizations were cited under EC.02.05.01, EP 9 for the same defect: circuit breakers labeled SPARE sitting in the ON position, and in one case, a panel legend that no longer matched reality.

2. Incomplete documentation of testing is treated as a failure to test.

Several findings were not about failing to test; they were about inventories that did not reconcile, contractor reports missing the NFPA reference, a device marked inaccessible and left untested, and a certification that devices passed with no list of which 99. EC.02.03.05 and EP 28 spell out the required documentation elements. Develop an audit tool to periodically check the list for required references.

3. Finding the problem, but no action is documented.

The most useful findings in this set were the absence of paper trails: an eyewash station documented as failing for six months of weekly checks, emergency lights logged as failed across months of testing with no action recorded, and generator fuel analyses returning out-of-range values that were not evaluated. Each one moved to Moderate or Widespread because the records proved the issue was known, but the resolution loop was not closed. Develop an audit tool to verify that logs are reviewed, the work order owner has signed and dated, and the corrective action is documented with a signature and date, along with details of what was done.

4. Leadership findings due to identified system issues.

LD.04.01.07, EP 1 was scored for failing to effectively manage policy implementation.  Accumulated, system findings from the environment of care can easily be cited in a Leadership standard at the Moderate/Pattern level. Ensure there is a standardized reporting process for senior leaders on the monthly audits performed, the corrective actions taken, and the completed corrective actions.

5. PCMH

PCMH option findings:  These findings are the most frequently cited, so hardwiring these standards and elements of performance will be the best strategy to avoid having to develop after-survey evidence of standards compliance.  For example, health literacy was not documented in 4 of 5 records; work history and occupational exposures were missing in 3 of 5 records; and self-management goals were absent from every chronic disease record reviewed. These EPs are scored once observed. Develop an audit checklist and periodically audit records for at least these three elements.  Report the findings to the clinic provider or administrator.

Your Survey Readiness Check

Develop a survey tracer audit checklist to include:

- Open electrical panels and confirm each breaker labeled SPARE is off, and the legend is accurate.

- Last twelve months of eyewash station checks and emergency lighting tests. For every failure recorded, locate the documented correction.

- Audit the most recent fire alarm testing report against the required documentation elements including the NFPA reference.

- Audit that the device inventory reconciles with the number of devices the contractor reports testing.

- During environmental rounds, check that any door marked as an exit opens in the direction of travel without a badge, key, or special knowledge.

- During environmental rounds, check any room converted to storage for a self-closing door and appropriate enclosure.

- Audit the high-alert medication list, then look where those medications are stored, including procedural areas and outpatient satellite areas. Confirm the labeling matches the policy.  Include the pharmacist in this audit.

- Review consents for procedures with laterality. Confirm that left, right, or bilateral is stated on the consent document itself.

- Audit a representative sample of staff files hired in the last year. Confirm that safety orientation is documented as completed before care was provided.

- PCMH:  Audit a representative sample of closed records for health literacy needs, work history, occupational exposures, and self-management goals with progress.

The findings in these surveys were not unusual and are frequently cited. Breakers, escutcheon rings, exit doors, testing logs, and findings in the medical records are usual observations by ambulatory surveyors. Every finding in this report can be added to a survey preparation checklist and periodically checked, reported and reviewed for corrective actions.