EMERGENCY RESPONSE PROCEDURES

Ontario Fire Code 2026 – Part 4 (Flammable & Combustible Liquids): The Almost Complete Guide to What Actually Changes on January 1

With January 1, 2026, now at our doorstep, here is a plain-English breakdown of nearly every significant change in Part 4 (O. Reg. 87/25) – Ontario’s first full harmonization with the 2020 National Fire Code in over two decades.

If you store, handle, dispense, or process more than 500 L total or more than 250 L of Class I liquids (gasoline, solvents, ethanol, etc.) in a fire compartment, these rules apply to you starting Day 1.

Who This Actually Affects (the real-world list)

- Chemical, paint, adhesive, plastics, and metal-working manufacturers

- Auto/fleet maintenance shops, body shops, dealerships

- Distilleries, breweries, large edible-oil users

- Construction contractors (roofing, flooring, painting, sealers)

- Bulk fuel terminals, backup diesel generators (hospitals, data centres, universities)

- Cannabis/hemp extraction facilities

- Printing plants, laboratories, waste & recycling operations

- Warehouses storing drums or totes of flammables

- Anyone with aboveground or underground tanks

The 13 Changes That Will Matter Most in 2026

- Mandatory Comprehensive Emergency Procedures (4.1.5.5 & 4.1.6.2) Written procedures covering fire, spill containment, vapour release, and environmental protection are now required everywhere the thresholds are exceeded. Process plants and refineries have zero exceptions.

- Mandatory Spill Control Procedure – Now Explicit & Detailed (New 4.1.6.4) Every site must have an approved, implemented, and prominently posted spill control procedure that specifically includes these eight elements: (a) operating procedures to prevent leaks/spills (b) ventilation requirements (c) control of ignition sources (d) containment & cleanup methods (dikes, absorbents, sand, etc.) (e) required PPE (rubber gloves/boots, SCBA, etc.) (f) chain of command and external notifications (g) preventive maintenance program (h) training for new and experienced staff

- Training Frequency – The Welcome Change Everyone Asked For (New 4.1.6.5) Staff must be trained on the spill control procedure and equipment use:

  - Initial training on assignment

  - Refresher at least once every three years -the old every-6-months retraining requirement has been removed – a genuine regulatory win.

- Spill & Fire-Water Runoff Control Plans must now show (typically on drawings) how spilled liquids and firefighting water are kept away from exits, air intakes, FDCs, neighbouring properties, and storm drains.

- Aboveground Tanks > 5,000 L 110 % secondary containment + vehicle-impact protection (bollards) are now mandatory.

- Underground Tanks & Piping Double-walled piping required on all new or full-replacement installations. Single-wall underground tanks are grandfathered only until December 31, 2031.

- Cannabis & Botanical Extraction (New 4.1.12) Hydrocarbon, >90 % ethanol, and supercritical CO₂ extraction facilities are now industrial occupancies – explosion-proof electrical, continuous gas detection, dedicated ventilation required.

- Dispensing & Transfer Upgrades Automatic overfill prevention + high-level alarms on tanks > 2,000 L; annual bonding/grounding continuity testing; breakaway hoses and automatic shut-off valves at vehicle islands.

- Indoor Storage Rooms & Cabinets Maximum 500 L Class I per fire compartment unless sprinklered; mechanical ventilation must be interlocked with lighting when > 250 L Class I is stored; updated signage requirements.

- Hot Work Restriction Only 45 L of Class I liquids permitted in open containers during welding, cutting, or grinding.

- Increased Separation Distances

  - Class I liquids in open systems → 6 m from ignition sources

  - Tank vent/relief valve terminations → 7.5 m from property lines/combustibles

- Record-Keeping Leak-detection logs, spill-kit inspections, bonding/grounding tests, training records (including spill control training) now explicitly required and subject to inspection.

- Grandfathering Is Limited Existing compliant installations stay legal until you modify, expand, or pull a new permit – then full 2026 rules apply immediately.

What Smart Companies Are Doing Right Now (December 2025)

- Updating or creating the 8-point spill control procedure and posting it wherever flammables are stored/used

- Revising training records (and enjoying the new 3-year cycle)

- Walking sites with the new tank tables (4.3.2.1–4.3.2.5) and checking secondary containment/bollards

- Adding spill flow arrows and containment details to site drawings

- Scheduling upgrades for single-wall underground piping and leak-detection systems

These changes close real gaps that caused major incidents over the past decade while delivering practical relief (especially the training frequency change).